Camfil USA, Inc. Washington, N.C. 200 Creekside Drive

Washington, N.C. 27889

Tel:   252-975-1141

Fax:  252-975-1041

www.camfil.com

# CityCarb I Specifications

  - General

  - - Air filters shall be compact 12” deep adsorber type with combination sorbent/particulate removal media, impact-resistant plastic end caps, plastic vertical support channels, and a nominal 1” header for front or side-access applications.

  - - Sizes shall be as noted on drawings or other supporting materials.

  - - Manufacturer shall provide evidence of facility certification to ISO 9001:2008. Filters shall be Camfil CityCarb I pleated V-Cell Cartridges or equal

# Construction

  - - Filter media shall be specifically manufactured for the removal of molecular and particulate contaminants. Sorbent shall be broad spectrum grade of carbon incorporating Rapid Adsorption Dynamics (RAD) designed for the removal of a wide range of odors, VOCs, and acid gases.

  - - Total media area shall be at least 0.040 square feet per rated cfm of filter.

  - - The media shall be formed into uniform pleats using hot-melt separators, assembled into multi media packs and bonded into a high impact resistant plastic frame to prevent air bypass.

  - - Media packs shall be sealed to the filter frame along all four sides

# Particulate and Initial Resistance Performance

  - - Initial resistance to airflow shall not exceed 0.54 inches w.g.(+/-10%)  at 500 feet per minute

velocity.

  - - The media shall have a particulate removal efficiency of MERV 15 when tested per the current standard of ASHRAE Standard 52.2

# Molecular Performance Testing

  - - Manufacturer shall provide results of efficiency testing against nitrogen dioxide, ozone, and toluene.

  - - Test to be conducted on full size complete filters when challenged with typical ambient concentrations, i.e. 1 to 5 ppm at 2,000 cfm.

  - - Gas detectors must have lower level of detection (LLoD) values <1 ppb.

  - - Filters to be tested by the manufacturer using a protocol in accordance with ASHRAE 145.2. Full details of test protocol to be included with photographic evidence.

  - – Filters shall have an initial removal efficiency of Toluene, per protocols specified above, of >90%

  - – Filters shall have an initial removal efficiency of Ozone, per protocols specified above, of >95%

  - – Filters shall have an initial removal efficiency of Nitrogen Dioxide, per protocols specified above, of >90%

  - – Filters shall have an initial removal efficiency of Sulphur Dioxide, per protocols specified above, of >90%

  - – Filters shall have an initial removal efficiency of Formaldehyde, per protocols specified above, of >75%

  - – Filters shall have an initial removal efficiency of Acetic Acid, per protocols specified above, of >95%